## Slide 1
1
AIU SMART CAMPUS
Energy Impact & Benchmark Analysis
Universities have already demonstrated measurable energy savings through smart sensing and automated control. The question is how much of that opportunity can be captured at AIU through an integrated cyber-physical control platform.
Estimates are benchmark-based projections, not measured AIU results | October 2026

## Slide 2
Executive summary
Sources: S1 (Lee & Kim 2020), S2–S12; AIU contract data A2–A3; model: AIU_Energy_Model. All AIU figures are estimates.
2
27.9–32.4%
Measured classroom savings, H University, Seoul (cooling / lighting)
≈43 GWh/yr
Benchmark-based AIU baseline (not measured)
5–13%
Defensible target on controllable energy (≈2.5–7.6% of total)
Evidence is real, but each number measures something different: lighting-only, HVAC-only, building, lab or campus programme.
Scenarios: 1.08 / 3.28 / 7.66 GWh per year (Conservative / Moderate / High-impact).
Our system controls lighting, HVAC set-points/shutdown and non-critical loads — not all campus energy.
Next step: validate with AIU meter data and a controlled on/off pilot.
Notes: Headline: demonstrated range is wide and scope-dependent; AIU defensible range is 5-13% of controllable energy.

## Slide 3
Problem: campuses run on schedules, people don't
Context: hot-climate campuses are cooling-dominated (S14); occupancy-driven control addresses the mismatch.
3
1
Occupancy ≠ schedule
Rooms are lit and cooled whether or not anyone is there.
2
Savings are rarely quantified per campus
Published results rarely translate to a specific campus size.
3
Energy is only one risk
Automated physical actions also need verification, evidence and audit.
Question: how much energy could AIU Smart Campus realistically save at Alamein International University?

## Slide 4
Existing university benchmarks
Sources S1–S12. Bars are NOT comparable averages: scope differs (see right). Targets/estimates are labelled.
4
Chart: 
| Seoul parking light | UC Irvine labs (avg) | UC Irvine NS-II | Utah Eyring (est.) | MSU Anthony Hall | Seoul class light | Seoul dorm RMS | Seoul class cooling | CMU/DOE (target) | Pace (program) | ACEEE edu. model | LBNL FDD median
Saving % | 77.6 | 61 | 51 | 44 | 34 | 32.4 | 28.2 | 27.9 | 20 | 18 | 11 | 9
Lighting/HVAC end-use
Seoul 28–78%
Building retrofit
MSU 34%
Laboratory
UCI 51–61%
Campus programme
Pace ≈18%, LBNL 9%
Target / estimate
CMU 20%, Utah 44%
Notes: Chart: do not average. Cmu is a target; Utah an estimate; Colorado Mesa excluded (geothermal).

## Slide 5
Korean university experimental study
S1: Lee & Kim, Sustainability 12(22):9471 (2020). H University, Seoul, South Korea — not a U.S. study. Measured ON/OFF, 4–7 weeks per test.
5
77.6%
Parking lighting (918.66 m², dimmable, 6 wks)
32.4%
Classroom lighting (3 rooms, 4 wks)
27.9%
Classroom cooling (EHP)
28.2%
Dormitory, key-card RMS (10 vs 120 rooms)
Read with care
Application-specific, shoulder-season (May–June, Oct–Nov), one campus.
Dorm saving is reference-calibrated: 40.0 / 16.2 / 30.9% in the three weeks.
Per-area daily values (25.0 / 55.0 / 39.5 / 142.4 Wh/m²·day) — no annual campus total.
Notes: Dorm = key-card RMS (not PIR). Classroom results: two on/off pairs. Do not extrapolate parking 77.6%.

## Slide 6
U.S. university benchmarks — what each number means
S2–S12 (U.S. DOE Better Buildings, UCI News, LBNL, ACEEE). Colorado Mesa (geothermal, 14.86M kWh/yr) excluded from savings-rate selection.
6
MSU Anthony Hall
34%
Building-level multi-measure retrofit; $536k/yr
UC Irvine Smart Labs
51–61%
Lab ventilation redesign; NS-II excludes process loads
Pace University
≈18%
Campus programme; 26M kWh + 1M therms through 2022
LBNL SEA campaign
9% median
Analytics software; 6,500 buildings
Univ. of Utah Eyring
44% (est.)
Lab/classroom retrofit — estimated
CMU / DOE
20% target
Occupancy sensing + MPC — not a result

## Slide 7
AIU campus scale — three numbers, three meanings
A1–A6: SIAC, REDCON, REC Consultants, Amwal Al Ghad 2018, Architizer. Current operating area and student count: not publicly verified.
7
CURRENT / operating
10 faculty buildings, 4 accommodation towers, library, admin, hospitals (reported)
Operating built-up area: not publicly verified
Student count: not publicly verified
CONTRACT BUA (documented)
263,020 m² — REDCON scope: 4 educational + 2 housing buildings
174,000 m² — SIAC package (REC says 100,390 m²)
Not the campus total; not additive without confirmation
PLANNED / master plan
≈150 acres land area (acres per source; user cites feddan)
Third phase: 3 buildings + major hospital, unquantified
≈15,000 students at full build-out
Model uses 263,020 m² as the central reference area; 174,000 and 437,020 m² as sensitivities.
Notes: 263,020 = REDCON contract BUA; 174,000 = SIAC package; 100,390 = REC for same package as SIAC (unreconciled). ~150 acres is land area.

## Slide 8
AIU baseline estimate: area × energy-use intensity
S14 (hot-climate university EUIs: Sharjah ≈165, Dammam 167–217, Al-Rajhi 145–155 kWh/m²·yr). Benchmark-based estimated baseline, NOT actual AIU consumption.
8
Annual energy = built-up area × EUI
BUA case | 130 kWh/m²·yr | 165 (mid) | 215 kWh/m²·yr
174,000 m² | 22.62 GWh | 28.71 GWh | 37.41 GWh
263,020 m² (central) | 34.19 GWh | 43.40 GWh | 56.55 GWh
437,020 m² (unverified sum) | 56.81 GWh | 72.11 GWh | 93.96 GWh
Central case: 43,398,300 kWh = 43,398 MWh = 43.4 GWh per year — confidence MEDIUM (area LOW–MEDIUM).
Controllable energy ≠ total energy: only lighting, HVAC, plug and scheduled loads are in scope.

## Slide 9
Conservative scenario
Model: saved = baseline × controllable share × coverage × saving rate on controlled loads. Rates: S1, S6, S10–S13. Estimates, subject to AIU baseline validation.
9
50%
Controllable share of total
50%
Automation coverage (project target)
10%
Saving on controlled loads
1.08 GWh
Annual energy saved
2.5% of total | 5.0% of controllable | 90,413 kWh per month
Why this scenario is reasonable
10% matches LBNL median FDD saving (9%) and ACEEE education occupancy model (11%).
Half of the controllable load is covered; the rest awaits sensors/actuators.
Most defensible lower bound — near-certain to be exceeded if coverage is achieved.
Notes: Cons 10% on controlled loads.

## Slide 10
Moderate scenario
Model: saved = baseline × controllable share × coverage × saving rate on controlled loads. Rates: S1, S6, S10–S13. Estimates, subject to AIU baseline validation.
10
60%
Controllable share of total
70%
Automation coverage (project target)
18%
Saving on controlled loads
3.28 GWh
Annual energy saved
7.6% of total | 12.6% of controllable | 273,409 kWh per month
Why this scenario is reasonable
18% sits at Pace's programme average (≈18%), CMU/DOE target (20%) and Crete (>20%).
70% coverage is a realistic first-phase deployment target.
Together with Conservative, forms the defensible planning range: 5–13% of controllable energy.
Notes: Mod 18%.

## Slide 11
High-impact scenario
Model: saved = baseline × controllable share × coverage × saving rate on controlled loads. Rates: S1, S6, S10–S13. Estimates, subject to AIU baseline validation.
11
70%
Controllable share of total
90%
Automation coverage (project target)
28%
Saving on controlled loads
7.66 GWh
Annual energy saved
17.6% of total | 25.2% of controllable | 637,955 kWh per month
Why this scenario is reasonable
28% reflects Korean measured end-use results (27.9–32.4%, dorm 28.2%).
Requires 90% coverage and sustained results; 30%+ is NOT assumed (S2's 34% is a multi-measure retrofit).
Upper bound — not a plan. 51–61% lab savings need ventilation redesign our system does not do.
Notes: High 28%.

## Slide 12
Expected annual energy savings
Model output; baseline 43.4 GWh/yr (benchmark-based). Category shares of 263,020 m² are a labelled assumption (LOW confidence).
12
Chart: By scenario
| Conservative | Moderate | High-impact
GWh saved / year | 1.08 | 3.28 | 7.66
Chart: Moderate case by building category (MWh/yr)
| Academic | Laboratories (teaching) | Admin | Dormitories | Sports
Moderate | 1422 | 122 | 444 | 820 | 122

## Slide 13
Five-year impact
Flat annual saving from first full year; no ramp-up, degradation, growth or tariff escalation. Estimates.
13
Chart: Cumulative GWh saved
| Y0 | Y1 | Y2 | Y3 | Y4 | Y5
Conservative | 0 | 1.08 | 2.17 | 3.25 | 4.34 | 5.42
Moderate | 0 | 3.28 | 6.56 | 9.84 | 13.12 | 16.4
High-impact | 0 | 7.66 | 15.31 | 22.97 | 30.62 | 38.28
5.42 GWh
Conservative, 5 years
16.40 GWh
Moderate, 5 years
38.28 GWh
High-impact, 5 years

## Slide 14
Financial and CO₂ impact — scenarios
E1: EgyptERA tariff from April 2026, medium-voltage 'other users' 255 Pt/kWh = EGP 2.55/kWh (excl. 3 Pt stamp and fees). AIU category not verified. CO₂: Ember 0.563 kg/kWh (E2, secondary access; re-confirm).
14
 | Conservative | Moderate | High-impact
Annual saving (EGP million) | 2.8 | 8.4 | 19.5
5-year saving (EGP million) | 13.8 | 41.8 | 97.6
Annual @ EGP 2.74 LV (million) | 3.0 | 9.0 | 21.0
CO₂ avoided per year (t, indicative) | 611 | 1,847 | 4,310
Gross energy-cost saving only: capital, maintenance and installation costs are not included, so no payback is claimed. Constant tariff, no escalation. CO₂ = kWh × 0.563 kg/kWh (Ember, lifecycle basis; confidence MEDIUM).

## Slide 15
Smart Lab case: classrooms vs laboratories
S3–S4 (UC Irvine), S11 (ACEEE), S1 (Seoul). Our planning rates for labs: 5 / 10 / 20% on a 40% controllable share.
15
General classrooms
Lighting + cooling follow occupancy
Seoul: 32.4% lighting, 27.9% cooling
ACEEE education model: 11%
Our system: occupancy-confirmed shutdown — fits directly
Laboratories
Ventilation, exhaust and process loads dominate
UC Irvine: 61% avg (10 labs), 51% NS-II — via variable air-change control + air-quality + occupancy sensing
ACEEE lab model: 40%
Our system: non-critical loads only; critical devices guarded — we do not claim UCI-level savings
Notes: Lab savings come from air-change-rate control; our system acts on non-critical loads only.

## Slide 16
Why this is valid, and the research gap
Existing evidence: S1–S13. Gap statement is limited to the sources reviewed; it is not a claim that no such system exists.
16
Proven by existing research
Occupancy sensing works
Lighting and HVAC automation work
Room management works
University buildings achieve measurable savings
Typical focus in reviewed work
Lighting · HVAC · occupancy · energy monitoring · single buildings · laboratory optimisation
Our contribution: integration
Physical sensing + context + verification
Automation decision + physical control
Energy measurement
Security, access, evidence
Investigation and auditability
— in one Command Center

## Slide 17
Why AIU Smart Campus
Pipeline: SENSE → ANALYZE → VERIFY → DECIDE → ACT → MONITOR (deterministic rules, not AI/ML). Prototype status: no measured AIU kWh savings yet.
17
SENSE
PIR + telemetry
ANALYZE
zone + schedule
VERIFY
confirm empty
DECIDE
rule + guard
ACT
non-critical loads
MONITOR
status + energy
Verification before action cuts nuisance shutdowns — the usual reason occupancy control gets disabled.
Zone context and CRITICAL-device guard make one sensor drive safe, different actions for classrooms, labs and dorms.
Energy readings + automation logs turn assumed savings into measurable before/after kWh.
Access control, evidence and investigation make automated physical actions auditable.
Next: 12 months of AIU meter data · alternate-week ON/OFF pilot with reference rooms · weather-normalised kWh · report with confidence intervals.
Notes: Be honest: prototype; commands may show queued_no_broker / COMMAND_FAILED without hardware.

## Slide 18
Conclusion
All AIU figures are benchmark-based projections to be validated against AIU meter data.
18
Evidence
Seoul measured 27.9–32.4% on classroom end-uses and 28.2% in dorms; U.S. campus-level programmes show ≈9–20%.
Defensible AIU target
5–13% of controllable energy ≈ 1.08–3.28 GWh/yr (2.5–7.6% of total); ≈ EGP 2.8–8.4 million/yr.
Biggest potential
Academic buildings and dormitories; labs less under non-critical-load control.
Prove it
12 months of meter data, sub-metering, alternate-week ON/OFF pilot with reference rooms, weather normalisation.
Based on comparable university implementations, AIU could potentially target an estimated 5–13% reduction in controllable energy, subject to validation through actual baseline measurements.